Chel - I / Electro-Mechanical Works / 002	   		    	23rd December 2010

Sub:	Tender for “Electro-Mechanical (E&M) works for Construction of 7.5 MW 
(3x2.5 MW)+20% continuous overload Chel – I Hydro-electric Project, District Darjeeling, West Bengal” Bid No. CHEL-I / Electro-Mechanical Works / 002 dated 8th November 2010

Addendum - 3

Dear Sir,

Some of the Bidders have been seeking clarifications on the heads to be considered.

Bidders may note that following are the Salient Levels to be considered for computation of heads :

1.	FRL at Chel Weir			=	EL 766.0 m

2.	HFL at Chel Weir			=	EL 769.0 m (inconsequential for head calculation)

3.	Maximum Water Level at Forebay	=	EL 763.4 m

4.	Normal Water Level at Forebay		=	EL 760.8 m

5.	MDDL in Forebay			=	EL 759.8 m

6.	Normal Tail Water Level		=	EL 506.0 m

7.	Maximum Tail Water Level		=	EL 507.3 m

Based upon on the above noted salient levels and considering the head loss in the system, center line of the units has been proposed at EL 508.92 m, which is 1.62 m above the maximum TWL and the rated head has been calculated as 238.88 m.

Since all the drawings, duly dimensioned and the discharge parameters are available in the tender documents, the Bidders are advised to make their own calculations for turbine setting, ensuring that centerline of the Pelton Wheel runner is at least 1.6 m above the maximum TWL.

No further queries on the head & discharge parameters to be adopted shall be entertained.

The Addendum No. 3 thus issued shall be part of the bidding documents and shall be duly acknowledged by the Bidder.

Two copies of this addendum duly signed in acceptance shall be submitted along with the bid documents in the manner prescribed under Sub-section D of Instructions to Bidders.  All other terms and conditions specified shall remain unchanged.

We now look forward to your active participation in the Bid.

Thanking you,

For and on behalf of

PCM Hydel Power Corporation Limited

Authorized Signatory